**SIDEWINDER EXM2 MONITOR (7100SDX2)**

**Product Specification**

An Elkhart Brass monitor shall be provided that features an integrated Wi-Fi communication system that allows for configuration and diagnostics via a Wi-Fi capable device. The monitor shall be constructed from durable, hard anodized, lightweight Elk-O-Lite® material with a variable cross-sectional and vaned waterway for flows up to 750 gpm (3000 lpm) at 250 psi (17.5 bar) for continuous duty; shall be constructed with thrust rods and thrust bearings on both horizontal and vertical rotational joints for improved product longevity; shall be configured with female 2.5“ NPT or 2.5” BSPT style inlet connection; shall be configured with male 2.5“ NHT or 2.5” BSPP style outlet connection; shall have two (2) gear motors that allow for simultaneous vertical and horizontal adjustment, one motor shall control up to 350 degree horizontal rotation while the other motor shall control up to 135 degrees vertical travel (-45 degree to +90 degree vertical rotation from horizontal); horizontal and vertical motors shall have a manual override device for use in the event of power failure; electric controls shall be NEMA 4 rated and allow for programmable horizontal center position, vertical and horizontal stops, stow and deploy positions, keep out zones, and motor speeds fast or slow; electric control shall allow for horizontal and vertical oscillation, electric control shall be CAN compatible; shall be compatible with both 12VDC and 24VDC power supply; shall include auxiliary output for driving an external device (i.e. light or camera).