## 1.5" UR Valves
© Elkhart Brass Mfg. Co., Inc
[7 empty] | Created by: Eric Drummond 5/14/02 | Last Modified: 5/14/02
1.5" Pressure-Matic Valve Selection Table
| Static Inlet Pressure (PSI) |  |  | 0 | ¬
| Residual Inlet Pressure (PSI) |  |  | 0 | ¬ | Enter values in these three fields
| Flow Rate (GPM) |  |  | 0 | ¬
Models: UR-20 & 25
| Avail-ability | Valve Type | Static Outlet Pressure (PSI) | Residual Outlet Pressure (PSI) |  |  |  | W | X | Y | YZ | Z | ZA | ZB | ZZ | ZZA | Static
[7 empty] | Static Reduction Ratio | 3.7825 | 3.2888 | 2.6667 | 2.2399 | 1.8576 | 1.6908 | 1.5 | 1.3089 | 1.1385 |  | X1 | Y1 | X2 | Y2 | M
[7 empty] | Residual Reduction Ratio (50-200 GPM) | 4.7548 | 4.0252 | 3.1621 | 2.5682 | 2.0921 | 1.8732 | 1.6345 | 1.4008 | 1.1854 | W | 106.9 | 390 | 22.3 | 70 | 3.7825
| Available | W | 3.7938 | N/A |  |  | Residual Reduction Ratio (200-250 GPM) | 4.8333 | 3.951 | 3.4898 | 2.6753 | 1.9204 | 1.7304 | 1.543 | 1.3428 | 1.1551 | X | 124.2 | 390 | 26.9 | 70 | 3.2888
| Available | X | 5.6156 | N/A | [12 empty] | Y | 151.5 | 390 | 31.5 | 70 | 2.6667
| Available | Y | 5.25 | N/A | [12 empty] | YZ | 173 | 380 | 34.6 | 70 | 2.2399
| Available | YZ | 3.3484 | N/A | [12 empty] | Z | 171.5 | 310 | 42.3 | 70 | 1.8576
| Available | Z | 4.6167 | N/A | [12 empty] | ZA | 171.9 | 280 | 47.7 | 70 | 1.6908
| Available | ZA | 6.3 | N/A | [12 empty] | ZB | 171.9 | 250 | 51.9 | 70 | 1.5
| Available | ZB | 5.2333 | N/A | [12 empty] | ZZ | 174.6 | 220 | 60 | 70 | 1.3089
| Available | ZZ | 6.52 | N/A | [12 empty] | ZZA | 172.3 | 190 | 66.9 | 70 | 1.1385
| Available | ZZA | 5.4167 | N/A
Residual 50-200
[18 empty] | X1 | Y1 | X2 | Y2 | M
| Notes | [15 empty] | W | 74.2 | 390 | 6.9 | 70 | 4.7548
1. | After entering inlet pressures and flow rate, check the "Availability" | [15 empty] | X | 91.4 | 390 | 11.9 | 70 | 4.0252
| column for valve availability. Valve availability is based on the static | [15 empty] | Y | 118.5 | 390 | 17.3 | 70 | 3.1621
| outlet pressure. Elkhart Brass does not recommend exceeding | [15 empty] | YZ | 144.2 | 390 | 19.6 | 70 | 2.5682
| a static outlet pressure of 165 psi. | [15 empty] | Z | 171.9 | 370 | 28.5 | 70 | 2.0921
2. | A value of "N/A" in the "Residual Outlet Pressure (PSI)" column | [15 empty] | ZA | 172.3 | 330 | 33.5 | 70 | 1.8732
| means that the maximum flow rate for the valve has been exceeded. | [15 empty] | ZB | 172.3 | 290 | 37.7 | 70 | 1.6345
3. | Outlet pressures shown are subjet to a tolerance of +/-10% | [15 empty] | ZZ | 172.7 | 250 | 44.2 | 70 | 1.4008
[17 empty] | ZZ | 172.7 | 250 | 44.2 | 70 | 1.4008
[17 empty] | ZZA | 169.2 | 210 | 51.1 | 70 | 1.1854
Residual 200-250
[18 empty] | X1 | Y1 | X2 | Y2 | M
[17 empty] | W | 61.9 | 390 | 1.9 | 100 | 4.8333
[17 empty] | X | 81.9 | 390 | 8.5 | 100 | 3.951
[17 empty] | Y | 100 | 390 | 16.9 | 100 | 3.4898
[17 empty] | YZ | 129.6 | 390 | 21.2 | 100 | 2.6753
[17 empty] | Z | 172.7 | 380 | 26.9 | 100 | 1.9204
[17 empty] | ZA | 171.4 | 340 | 32.7 | 100 | 1.7304
[17 empty] | ZB | 173.8 | 310 | 37.7 | 100 | 1.543
[17 empty] | ZZ | 172.3 | 270 | 45.7 | 100 | 1.3428
[17 empty] | ZZA | 173.5 | 240 | 52.3 | 100 | 1.1551

## 2.5" UR Valves
© Elkhart Brass Mfg. Co., Inc
[7 empty] | Created by: Eric Drummond 5/14/02 | Last Modified: 5/14/02
2.5" Pressure-Matic Valve Selection Table
| Static Inlet Pressure (PSI) |  |  | 0 | ¬
| Residual Inlet Pressure (PSI) |  |  | 0 | ¬ | Enter values in these three fields
| Flow Rate (GPM) |  |  | 0 | ¬
Models: UR-20 & 25
| Avail-ability | Valve Type | Static Outlet Pressure (PSI) | Residual Outlet Pressure (PSI) |  |  |  | A | B | C | CD | D | DE | E | EF | F | Static |  |  |  | Residual 100-200 Straight
[7 empty] | Static Reduction Ratio | 4 | 3.218 | 2.667 | 2.317 | 2.08 | 1.885 | 1.696 | 1.398 | 1.326 |  | X | Y |  |  | X | Y
[7 empty] | Residual Reduction Ratio (50-400 GPM) | 4.356 | 3.571 | 2.966 | 2.526 | 2.25 | 2 | 1.765 | 1.523 | 1.353 | A | 97 | 380 |  | A | 60 | 290
| Available | A | 2 | N/A |  |  | Residual Reduction Ratio (400-500 GPM) | 4.286 | 3.333 | 3.027 | 2.653 | 2.261 | 1.952 | 1.689 | 1.445 | 1.238 | B | 115 | 370 |  | B | 65 | 260
| Available | B | 0.021753 | N/A | [12 empty] | C | 140 | 380 |  | C | 90 | 310
| Available | C | -2.4822 | N/A | [12 empty] | CD | 120 | 280 |  | CD | 135 | 390
| Available | CD | -0.84592 | N/A | [12 empty] | D | 100 | 210 |  | D | 150 | 380
| Available | D | -0.96154 | N/A | [12 empty] | DE | 170 | 320 |  | DE | 107.5 | 230
| Available | DE | 0.23873 | N/A | [12 empty] | E | 125 | 210 |  | E | 172.3 | 310
| Available | E | 1.1792 | N/A | [12 empty] | EF | 130 | 190 |  | EF | 145 | 230
| Available | EF | -5.9084 | N/A | [12 empty] | F | 155 | 200 |  | F | 165 | 230
| Available | F | 4.1704 | N/A
[17 empty] | Residual 50-400 Angle |  |  |  | Residual 200-300 Straight
| Models: UR-20-S | [16 empty] | X | Y |  |  | X | Y
| Avail-ability | Valve Type | Static Outlet Pressure (PSI) | Residual Outlet Pressure (PSI) |  |  |  | A | B | C | CD | D | DE | E | EF | F | A | 50 | 230 |  | A | 65 | 350
[7 empty] | Static Reduction Ratio | 4 | 3.218 | 2.667 | 2.317 | 2.08 | 1.885 | 1.696 | 1.398 | 1.326 | B | 95 | 350 |  | B | 55 | 254
[7 empty] | Residual Reduction Ratio (50-100 GPM) | 3.833 | 3.778 | 3.317 | 2.72 | 2.421 | 1.989 | 1.667 | 1.455 | 1.304 | C | 120 | 370 |  | C | 102.5 | 370
| Available | A | 2 | N/A |  |  | Residual Reduction Ratio (100-200 GPM) | 4.381 | 3.8 | 3.3 | 2.833 | 2.5 | 2.049 | 1.714 | 1.5 | 1.314 | CD | 115 | 300 |  | CD | 80 | 249
| Available | B | 0.021753 | N/A |  |  | Residual Reduction Ratio (200-300 GPM) | 4.545 | 3.946 | 3.333 | 2.8 | 2.4 | 1.957 | 1.692 | 1.488 | 1.31 | D | 130 | 300 |  | D | 140 | 360
| Available | C | -2.4822 | N/A |  |  | Residual Reduction Ratio (300-400 GPM) | 5.76 | 4 | 2.98 | 2.5 | 2.217 | 1.95 | 1.759 | 1.51 | 1.31 | DE | 127 | 260 |  | DE | 132.5 | 290
| Available | CD | -0.84592 | N/A | [12 empty] | E | 110 | 200 |  | E | 135 | 260
| Available | D | -0.96154 | N/A | [12 empty] | EF | 135 | 210 |  | EF | 162.5 | 270
| Available | DE | 0.23873 | N/A | [12 empty] | F | 125 | 170 |  | F | 140 | 210
| Available | E | 1.1792 | N/A
| Available | EF | -5.9084 | N/A | [12 empty] | Residual 400-500 Angle |  |  |  | Residual 300-400 Straight
| Available | F | 4.1704 | N/A | [13 empty] | X | Y |  |  | X | Y
[17 empty] | A | 60 | 330 |  | A | 40 | 305
[17 empty] | B | 70 | 290 |  | B | 80 | 392
| Notes | [15 empty] | C | 60 | 230 |  | C | 85 | 330
1. | After entering inlet pressures and flow rate, check the "Availability" | [15 empty] | CD | 120 | 350 |  | CD | 125 | 380
| column for valve availability. Valve availability is based on the static | [15 empty] | D | 100 | 250 |  | D | 145 | 385
| outlet pressure. Elkhart Brass does not recommend exceeding | [15 empty] | DE | 44.2 | 100 |  | DE | 120 | 290
| a static outlet pressure of 165 psi. | [15 empty] | E | 125 | 220 |  | E | 165 | 340
2. | A value of "N/A" in the "Residual Outlet Pressure (PSI)" column | [15 empty] | EF | 125 | 190 |  | EF | 120 | 230
| means that the maximum flow rate for the valve has been exceeded. | [15 empty] | F | 150 | 200 |  | F | 165 | 261
3. | Outlet pressures shown are subjet to a tolerance of +/-10% | [15 empty] | ZZ | 172.7 | 250 | 44.2 | 70 | 1.4008
Residual 50-100 Straight
[18 empty] | X | Y
[17 empty] | A | 65 | 300
[17 empty] | B | 85 | 330
[17 empty] | C | 100 | 340
[17 empty] | CD | 105 | 300
[17 empty] | D | 150 | 370
[17 empty] | DE | 80 | 170
[17 empty] | E | 54.6 | 100
[17 empty] | EF | 130 | 200
[17 empty] | F | 170 | 230